## Открытые
Открытые станции - 400 V / 50 Hz - 4 poles
GRUPPI ELETTROGENI APERTI - Motori Diesel raffreddati ad acqua - 400 V / 50 Hz - 4 poli
Genset model | Go to options | Power | Govern. | Cylinder | Asp. | Displ. (l) | POWER |  |  |  | Ручной запуск | Автомат | Без панели | Экологический класс | Size |  |  | Масса
|  | Stand-by |  |  |  |  | 1500 RPM |  | 1800 RPM | [5 empty] | Габаритные размеры
Modello gruppo elettrogeno |  | kWa | Regolat. | Cilindri | Asp. | Cilin. (l) | Prime (2) | Stand-by (3) | Prime (2) | Stand-by (3) | Розница | Розница | Розница |  | mm
|  | (4) |  |  |  |  | Kw (kVA) | Kw (kVA) | Kw (kVA) | Kw (kVA) |  |  |  |  | L | W | H | kg.
GE F3230 MA.R980 |  | 30 | mecc | 4 L | n.a. | 3.2 | 24 (30) | 26,5 (33) | - - | - - | 10522 | 11006 | 9411 | Stage II | 1833 | 730 | 1416 | ~ 590
GE F3240 MA.R980 |  | 40 | mecc | 4 L | Tc | 3.2 | 32 (40) | 35 (44) | - - | - - | 11232 | 11716 | 10218 | Stage II | 1833 | 730 | 1416 | ~ 635
GE F3250 MA.R980 |  | 50 | mecc | 4 L | Taa | 3.2 | 40 (50) | 44 (55) | - - | - - | 11778 | 12285 | 10733 | Stage II | 1833 | 730 | 1416 | ~ 730
GE NEF45 MA.R980 |  | 45 | mecc | 4 L | n.a. | 4.5 | 36 (45) | 40 (50) | 40 (50) | 44 (55) | 11236 | 12542 | 10592 | Not emiss. | 2303 | 730 | 1285 | ~ 852
GE NEF50 M.R980 |  | 50 | mecc | 4 L | n.a. | 4.5 | 40 (50) | 44 (55) | - - | - - | 11661 | 11895 | 10202 | Stage II | 2303 | 730 | 1285 | ~ 853
GE NEF60 MA.R980 |  | 60 | mecc | 4 L | n.a. | 4.5 | 48 (60) | 53 (66) | 53 (66) | 58(73) | 13018 | 13545 | 11591 | Stage II | 2303 | 730 | 1322 | ~ 886
GE NEF75 MA.R980 |  | 75 | mecc | 4 L | Tc | 4.5 | 60 (75) | 66 (82) | 60 (75) | 66 (82) | 13412 | 13946 | 11926 | Not emiss. | 2303 | 730 | 1322 | ~ 902
GE NEF80 M.R980 |  | 80 | mecc | 4 L | Tc | 4.5 | 64 (80) | 70,4 (88) | - - | - - | 13182 | 13716 | 11696 | Stage II | 2303 | 730 | 1322 | ~ 903
GE NEF85 MA.R980 |  | 85 | mecc | 4 L | Tc | 4.5 | 68 (85) | 75 (94) | 80 (100) | 88 (110) | 14645 | 15062 | 12784 | Stage II | 2303 | 730 | 1475 | ~ 1130
GE NEF100 MA.R980 |  | 100 | mecc | 4 L | Taa | 4.5 | 80 (100) | 88 (110) | 88 (110) | 97 (121) | 14999 | 15421 | 13143 | Not emiss. | 2303 | 730 | 1475 | ~ 1160
GE NEF120 M.R980 |  | 120 | mecc | 4 L | Taa | 4.5 | 96 (120) | 105,6 (132 | - - | - - | 14820 | 15241 | 12964 | Not emiss. | 2303 | 730 | 1475 | 1160
GE NEF125 M.R980 |  | 125 | mecc | 6 L | Tc | 6.7 | 100 (125) | 110 (138) | 116 (138) | 128 (160) | 16973 | 17417 | 15066 | Stage II | 2800 | 780 | 1423 | ~ 1300
GE NEF130 MA.R980 |  | 130 | mecc | 6 L | Taa | 6.7 | 104 (130) | 114 (143) | 116 (143) | 128 (160) | 17417 | 17862 | 15506 | Stage II | 2800 | 780 | 1423 | ~ 1315
GE NEF160 MA.R980 |  | 160 | mecc | 6 L | Taa | 6.7 | 128 (160) | 141 (176) | 136 (170) | 150 (187) | 17979 | 18428 | 16080 | Not emiss. | 2800 | 780 | 1423 | ~ 1440
GE NEF170 M.R980 |  | 170 | mecc | 6 L | Taa | 6.7 | 136 (170) | 149,6 (187) | - - | - - | 17706 | 18155 | 15807 | Not emiss. | 2800 | 780 | 1423 | 1440
GE NEF200 M.R980 |  | 200 | mecc | 6 L | Taa | 6.7 | 160 (200) | 176 (220) | - - | - - | n.a. | n.a. | n.a. | Stage II | - - | - - | - - | ~ - -
GE NEF200 EA.R980 |  | 200 | C.R. | 6 L | Taa | 6.7 | 160 (200) | 176 (220) | 180 (225) | 198 (248) | 21996 | 22441 | 19562 | Not emiss. | 2800 | 780 | 1423 | ~ 1570
GE CURSOR250 ED.R990 |  | 250 | C.R. | 6 L | Taa | 8.7 | 200 (250) | 220 (275) | - - | - - | 25471 | 25994 | 23115 | Stage II | 3020 | 1055 | 1690 | ~ 1950
GE CURSOR250 E.R990 |  | 250 | C.R. | 6 L | Taa | 8.7 | 200 (250) | 220 (275) | 216 (270) | 238 (297) | n.a. | n.a. | n.a. | Not emiss. | - - | - - | - - | ~ - -
GE CURSOR300 E.R990 |  | 300 | C.R. | 6 L | Taa | 8.7 | 240 (300) | 264 (330) | - - | - - | n.a. | n.a. | n.a. | Not emiss. | - - | - - | - - | ~ - -
GE CURSOR300 ED.R990 |  | 300 | EUI | 6 L | Taa | 10.3 | 240 (300) | 264 (330) | 280(330) | 308 (363) | 35549 | 36075 | 32627 | Stage II | 3020 | 1055 | 1690 | ~ 2500
GE CURSOR350 EA.R990 |  | 350 | EUI | 6 L | Taa | 12.9 | 280(350) | 308 (385) | 304 (380) | 334 (418) | 37120 | 37643 | 34199 | Stage II | 3526 | 1101 | 1858 | ~ 2650
GE CURSOR400 EA.R990 |  | 400 | EUI | 6 L | Taa | 12.9 | 320 (400) | 352 (440) | 336 (420) | 370 (462) | 38903 | 39109 | 36017 | Stage II | 3530 | 1286 | 1939 | ~ 2780
GE CURSOR500 ------- |  | 500 | EUI | 6 L | Taa | 12.9 | 400 (500) | 440 (550) | - - | - - | 52531 | 52737 | 49646 | Not emiss. | - - | - - | - - | ~ - -
CONFIGURATION : | L= in line/in linea - mecc= mechanical/meccanico - CR= Common rail - UEI = Electronic unit injectior | [9 empty] | Stage IIA | Not emissioned | Options not available
NA= Natural aspirated/aspirato - TC = Turbocharged/turbocompresso - TAA= turbocharged air cooled/turbocompresso con refrigerazione dell'aria
(2) | Prime Power (P.R.P.) = The prime Power is the maximum power available with varying loads for an unlimited number of hours. The average power output during a 24 h period of operation must not exceed 80% of the declared prime power between the prescribed maintenance intervals and at standard environmental conditions. A 10% overload is permissible for 1 hour every 12 hours of operation.
(3) | Stand-by Power (ISO3046 Fuel stop power) = This is the maximum power available for a period of 500 hours/year with a mean load factor of 90% of the declared stand-by power. No kind of overload is permissible for this use.
(4) | Ratings in accordance with ISO 8528. For duty at temperature over 40°C and/or altitude over 1000 meters must be considered a power derating factor. Contact the FPT sales organization
FPT INDUSTRIAL reserves the right to change the price list conditions without notice | [17 empty] | E. & O. E.
прайс-лист 2015

## В кожухе
Закрытые электростанции - 1500/1800 RPM - 50/60 Hz
GRUPPI ELETTROGENI INSONORIZZATI - Motori Diesel raffreddati ad acqua - 1500/1500 RPM - 50/60 Hz
Genset model | Go to options | Power | Govern. | Cylinder | Asp. | Displ. (l) | POWER |  |  |  | Ручной запуск | Автомат | Без панели | Экологический класс | Size |  |  | Масса
|  | Stand-by |  |  |  |  | 1500 RPM |  | 1800 RPM | [5 empty] | Размеры |  |  | Peso
Modello gruppo elettrogeno |  | kWa | Regolat. | Cilindri | Asp. | Cilin. (l) | Prime (2) | Stand-by (3) | Prime (2) | Stand-by (3) | Розница | Розница | Розница |  | mm
|  | (4) |  |  |  |  | Kw (kVA) | Kw (kVA) | Kw (kVA) | Kw (kVA) | Euro | Euro | Euro |  | L | W | H | kg.
GS F3230 |  | 30 | mecc | 4 L | n.a. | 3.2 | 24 (30) | 26,5 (33) | - - | - - | 12480 | 13173 | 11856 | Stage II | 2200 | 930 | 1450 | ~ 1010
GS F3240 |  | 40 | mecc | 4 L | Tc | 3.2 | 32 (40) | 35 (44) | - - | - - | 13347 | 13953 | 12753 | Stage II | 2200 | 930 | 1450 | ~ 1090
GS NEF45 |  | 45 | mecc | 4 L | n.a. | 4.5 | 36 (45) | 40 (50) | 40 (50) | 44 (55) | 14040 | 14647 | 13260 | Stage II | 2550 | 1030 | 1650 | ~ 1230
GS NEF50 n |  | 50 | mecc | 4 L | n.a. | 4.5 | 40 (50) | 44 (55) | - - | - - | 14196 | 14781 | 13416 | Not emiss. | 2550 | 1030 | 1650 | ~ 1315
GS NEF60 |  | 60 | mecc | 4 L | n.a. | 4.5 | 48 (60) | 53 (66) | 53 (66) | 58(73) | 14733 | 15340 | 13416 | Stage II | 2550 | 1030 | 1650 | ~ 1315
GS NEF75 |  | 75 | mecc | 4 L | Tc | 4.5 | 60 (75) | 66 (82) | 60 (75) | 66 (82) | 15773 | 16553 | 15210 | Stage II | 2900 | 1130 | 1800 | ~ 1420
GS NEF80 n |  | 80 | mecc | 4 L | Tc | 4.5 | 64 (80) | 70,4 (88) | - - | - - | 16146 | 16926 | 15600 | Not emiss. | 2900 | 1130 | 1800 | ~ 1460
GE NEF85 |  | 85 | mecc | 4 L | Tc | 4.5 | 68 (85) | 75 (94) | 80 (100) | 88 (110) | 16814 | 17594 | 16318 | Stage II | 2900 | 1130 | 1800 | ~ 1470
GE NEF100 |  | 100 | mecc | 4 L | Taa | 4.5 | 80 (100) | 88 (110) | 88 (110) | 97 (121) | 17333 | 18027 | 16587 | Stage II | 2900 | 1130 | 1800 | ~ 1555
GS NEF120 n |  | 120 | mecc | 4 L | Taa | 4.5 | 96 (120) | 105,6 (132 | - - | - - | 18330 | 19032 | 17316 | Not emiss. | 3400 | 1130 | 1800 | ~ 1750
GS NEF125 n |  | 125 | mecc | 6 L | Tc | 6.7 | 100 (125) | 110 (138) | 116 (138) | 128 (160) | 19934 | 20714 | 19305 | Not emiss. | 3400 | 1130 | 1800 | ~ 1755
GS NEF130 |  | 130 | mecc | 6 L | Taa | 6.7 | 104 (130) | 114 (143) | 116 (143) | 128 (160) | 20973 | 21753 | 20370 | Stage II | 3400 | 1130 | 1800 | ~ 1795
GS NEF160 |  | 160 | mecc | 6 L | Taa | 6.7 | 128 (160) | 141 (176) | 136 (170) | 150 (187) | 22533 | 23313 | 21509 | Stage II | 3400 | 1130 | 1800 | ~ 1845
GS NEF170 n |  | 170 | mecc | 6 L | Taa | 6.7 | 136 (170) | 149,6 (187) | - - | - - | 22932 | 23790 | 21918 | Not emiss. | 3400 | 1130 | 1800 | ~ 1860
GS NEF200 n |  | 200 | mecc | 6 L | Taa | 6.7 | 160 (200) | 176 (220) | - - | - - | 25350 | 26130 | 24648 | Not emiss. | 3400 | 1130 | 1800 | ~ 1880
GS NEF200 |  | 200 | C.R. | 6 L | Taa | 6.7 | 160 (200) | 176 (220) | 180 (225) | 198 (248) | 26000 | 26780 | 24620 | Stage II | 3400 | 1130 | 1800 | ~ 1900
GS CURSOR250 n |  | 250 | C.R. | 6 L | Taa | 8.7 | 200 (250) | 220 (275) | - - | - - | 35256 | 36426 | 33774 | Not emiss. | 3750 | 1430 | 2100 | ~ 3075
GS CURSOR250 |  | 250 | C.R. | 6 L | Taa | 8.7 | 200 (250) | 220 (275) | 216 (270) | 238 (297) | 36573 | 37267 | 34476 | Stage II | 3750 | 1430 | 2100 | ~ 3075
GS CURSOR300 n |  | 300 | C.R. | 6 L | Taa | 8.7 | 240 (300) | 264 (330) | - - | - - | 42744 | 43446 | 40560 | Not emiss. | 3900 | 1350 | 2130 | ~ 3120
GS CURSOR300 |  | 300 | EUI | 6 L | Taa | 10.3 | 240 (300) | 264 (330) | 280(330) | 308 (363) | 43853 | 44547 | 42159 | Stage II | 4850 | 1630 | 2500 | ~ 3450
GS CURSOR350 |  | 350 | EUI | 6 L | Taa | 12.9 | 280(350) | 308 (385) | 304 (380) | 334 (418) | 44720 | 45413 | 42650 | Stage II | 4850 | 1630 | 2500 | ~ 3600
GS CURSOR400 |  | 400 | EUI | 6 L | Taa | 12.9 | 320 (400) | 352 (440) | 336 (420) | 370 (462) | 47667 | 48533 | 46878 | Stage II | 4850 | 1630 | 2500 | ~ 3745
GS CURSOR500 n |  | 500 | EUI | 6 L | Taa | 12.9 | - - | - - | - - | - - | n.a. | n.a. | n.a. | Stage II | - - | - - | - - | ~ - -
CONFIGURATION : | L= in line/in linea - mecc= mechanical/meccanico - CR= Common rail - UEI = Electronic unit injectior | [9 empty] | Stage II | Not emissioned | Options not available
NA= Natural aspirated/aspirato - TC = Turbocharged/turbocompresso - TAA= turbocharged air cooled/turbocompresso con refrigerazione dell'aria
(2) | Prime Power (P.R.P.) = The prime Power is the maximum power available with varying loads for an unlimited number of hours. The average power output during a 24 h period of operation must not exceed 80% of the declared prime power between the prescribed maintenance intervals and at standard environmental conditions. A 10% overload is permissible for 1 hour every 12 hours of operation.
(3) | Stand-by Power (ISO3046 Fuel stop power) = This is the maximum power available for a period of 500 hours/year with a mean load factor of 90% of the declared stand-by power. No kind of overload is permissible for this use.
(4) | Ratings in accordance with ISO 8528. For duty at temperature over 40°C and/or altitude over 1000 meters must be considered a power derating factor. Contact the FPT sales organization
FPT INDUSTRIAL reserves the right to change the price list conditions without notice | [17 empty] | E. & O. E.
________________________ | [6 empty] | ________________________ |  |  |  |  | ________________________ |  |  | ________________________
SIGNATURE SALES KA | [6 empty] | SIGNATURE SALES MANAGER |  |  |  |  | SIGNATURE SALES ADMINISTRATOR |  |  | SIGNATURE SALES VP